Dominion PX PX2-1493 Tech Specs

|  | Click here for a PDF of the Data Sheet |
| --- | --- |
|  | Click here for a PDF of the Mechanical Drawing |

Input

·	Nominal voltage: 230V AC

·	Maximum line current: 32A

·	Rated current: 32A

·	Load capacity: 7.4 kVA

·	Frequency: 50-60 Hz

·	Plug type: IEC60309 32A

Output

·	Nominal voltage: 230V AC

·	Maximum current draw: 16A per circuit

·	Unswitched receptacles: 20 x IEC C-13, 4 x IEC C-19

·	Overload protection: 2 x single-pole 16A UL 489 circuit breakers

Metering

·	Inlet: Kilowatt hours (kWh), current (Amps), voltage, power (kVA, kW), power factor

·	Branch circuit breaker: Current, circuit breaker trip status

Rack Environment Management

·	Optional temperature and humidity sensors (RJ-12 connector)

Interface and Protocol Support

·	10-100 Mbps Ethernet (RJ-45 connector)

·	RS-232 serial (DB9 connector)

·	Feature/KVM (RJ-45 connector)

·	USB-A (host), USB-B (device)

·	SNMPv2, v3 TRAPs, GETs, SETs

·	Web browser and command line interface access

Mechanical

·	Rack space: Zero U

·	Mounting: Rack mount brackets included

·	Dimensions (WxDxH): 2.1" x 2.1" x 61.1"; 52 x 53 x 1539mm

·	Weight:  lbs;  kg

·	Display panel: Autoflip LED for PDU current (A), voltage, power (kW)

·	Sensor indicator

·	Line cord: 10 ft / 3 m

·	Color: Black powder coat

·	Shipping dimensions (WxDxH): 10.2" x 5.1" x 73.3"; 260 x 129 x 1860mm

·	Shipping weight:  lbs;  kg

Environmental Requirements

·	Operating temperature: 5-60 degrees Celsius

·	Humidity: 5-90% RH non-condensing

·	Altitude: 10,000 feet

Approvals

·	FCC Part 15, A; UL and c-UL 60950

·	RoHS compliant

Warranty

·	Two years, 100% parts and workmanship